{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":39,"n_cols":8,"rows_kept":39,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWLT-Q-XSA"]
[]
[]
[]
[]
["","","","","","EWLT100Q-XSA1","EWLT125Q-XSA1","EWLT160Q-XSA1"]
["Wydajność chłodnicza","Nom.","","","kW","90.2","116.9","155"]
["Regulacja wydajności","Metoda","","","","Etap","Etap","Etap"]
["Regulator wydajności","Minimalna wydajność","","","%","50","50","50"]
["Pobór mocy","Chłodzenie","","Nom.","kW","23.67","31.1","38.55"]
["EER","","","","","3.81","3.76","4.02"]
["Wymiary","Jednostka","","Głębokość","mm","1300","1300","1300"]
["","","","Wysokość","mm","1000","1000","1000"]
["","","","Szerokość","mm","1200","1200","1200"]
["Ciężar","Ciężar operacyjny","","","kg","382","428","482"]
["","Jednostka","","","kg","372","417","467"]
["Obudowa","Kolor","","","","Kość słoniowa","Kość słoniowa","Kość słoniowa"]
["","Materiał","","","","Stal galwanizowana","Stal galwanizowana","Stal galwanizowana"]
["Wodny wym. ciepła - parownik","Spadek ciś. wody","Chłodzenie","Nom.","kPa","17.16","17.93","19.55"]
["Sprężarka","Ilość","","","","2","2","2"]
["","Typ","","","","Scroll","Scroll","Scroll"]
["Zakres pracy","Strona wody","Parownik","Min.","°CDB","-15","-15","-15"]
["","","","Maks.","°CDB","30","30","30"]
["Poziom mocy akustycznej","Chłodzenie","","Nom.","dBA","80.99","84.19","85.99"]
["Poziom ciśnienia akustycznego","Chłodzenie","","Nom.","dBA","65.4","68.6","70.4"]
["Czynnik chłodniczy","Typ","","","","R-32","R-32","R-32"]
["","GWP","","","","675","675","675"]
["","Ilość","","","kg","0","0","0"]
["","Obwody","","Ilość","","1","1","1"]
["Połączenia instalacji rurowej","Wlot/wylot wody parownika (śr. zewn.)","","","","3\"","3\"","3\""]
["Zasilanie energią elektryczną","liczba faz","","","","3","3","3"]
["Zasilanie","Częstotliwość","","","Hz","50","50","50"]
["","Napięcie","","","V","400","400","400"]
["","Zakres napięcia","","Min.","%","-10","-10","-10"]
["","","","Maks.","%","+10","+10","+10"]
["Jednostka","Prąd rozruch.","","Jednostka-=-Prąd rozruch.-=-Maks.-=-A","A","221","345","363"]
["","Prąd roboczy","Chłodzenie","Nom.","A","42.1","50","60.7"]
["","","","Maks.","A","62","80","97"]
["","Maks. prąd jednostki dla wymiarowania przewodów","","","A","68","88","107"]