{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":12,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWH-J-SS"]
[]
[]
[]
[]
["","","","","","EWWH090J-SS","EWWH110J-SS","EWWH120J-SS","EWWH130J-SS","EWWH150J-SS","EWWH180J-SS","EWWH200J-SS"]
["Wydajność chłodnicza","Nom.","","","kW","88.77","107.1","115.1","133.5","150.1","181.6","200.6"]
["Regulacja wydajności","Metoda","","","","Bezstopniowa","Bezstopniowa","Bezstopniowa","Bezstopniowa","Bezstopniowa","Bezstopniowa","Bezstopniowa"]
["Regulator wydajności","Minimalna wydajność","","","%","25","25","25","25","25","25","25"]
["Pobór mocy","Chłodzenie","","Nom.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Wymiary","Jednostka","","Głębokość","mm","2684","2684","2684","2684","2684","2684","2684"]
["","","","Wysokość","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Szerokość","mm","913","913","913","913","913","913","913"]
["Ciężar","Ciężar operacyjny","","","kg","1211","1276","1378","1415","1473","1663","1675"]
["","Jednostka","","","kg","1177","1233","1334","1366","1416","1600","1607"]
["Obudowa","Kolor","","","","Kość słoniowa","Kość słoniowa","Kość słoniowa","Kość słoniowa","Kość słoniowa","Kość słoniowa","Kość słoniowa"]
["","Materiał","","","","Stal galwanizowana","Stal galwanizowana","Stal galwanizowana","Stal galwanizowana","Stal galwanizowana","Stal galwanizowana","Stal galwanizowana"]
["Wodny wymiennik ciepła - parownik","Typ","","","","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła"]
["","Objętość wody","","","l","14","18","14","17","20","26","26"]
["Wodny wym. ciepła - parownik","Spadek ciś. wody","Chłodzenie","Nom.","kPa","10.7","10.9","19.3","19.3","17.8","16.8","20.1"]
["Sprężarka","Ilość","","","","1","1","1","1","1","1","1"]
["","Typ","","","","Sprężarka jednośrubowa","Sprężarka jednośrubowa","Sprężarka jednośrubowa","Sprężarka jednośrubowa","Sprężarka jednośrubowa","Sprężarka jednośrubowa","Sprężarka jednośrubowa"]
["","Metoda uruchomienia_","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Zakres pracy","Strona wody","Parownik","Min.","°CDB","-5","-5","-5","-5","-5","-5","-5"]
["","","","Maks.","°CDB","25","25","25","25","25","25","25"]
["Poziom mocy akustycznej","Chłodzenie","","Nom.","dBA","95","95","95","95","95","95","95"]
["Poziom ciśnienia akustycznego","Chłodzenie","","Nom.","dBA","79","79","79","79","79","79","79"]
["Czynnik chłodniczy","Typ","","","","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)","R-1234(ze)"]
["","GWP","","","","1.4","1.4","1.4","1.4","1.4","1.4","1.4"]
["","Ilość","","","kg","18","35","34","37","37","38","38"]
["","Obwody","","Ilość","","1","1","1","1","1","1","1"]
["Połączenia instalacji rurowej","Wlot/wylot wody parownika (śr. zewn.)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Zakres efektywności energetycznej","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Zasilanie energią elektryczną","liczba faz","","","","3~","3~","3~","3~","3~","3~","3~"]
["Zasilanie","Częstotliwość","","","Hz","50","50","50","50","50","50","50"]
["","Napięcie","","","V","400","400","400","400","400","400","400"]
["","Zakres napięcia","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Maks.","%","10","10","10","10","10","10","10"]
["Jednostka","Prąd rozruch.","","Jednostka-=-Prąd rozruch.-=-Maks.-=-A","A","153","153","197","197","197","290","290"]
["","Prąd roboczy","Chłodzenie","Nom.","A","39","44","55","60","65","76","84"]
["","","","Maks.","A","75","90","100","114","143","158","178"]
["","Maks. prąd jednostki dla wymiarowania przewodów","","","A","83","100","112","127","159","176","198"]
["Uwagi","","","","","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB"]
["","","","","","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB"]
["","","","","","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825"]
["","","","","","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji."]
["","","","","","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy"]