{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":28,"n_cols":18,"rows_kept":28,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-VZXS"]
[]
[]
[]
[]
["","","","","EWWS450VZXSA1","EWWS490VZXSA1","EWWS600VZXSA1","EWWS700VZXSA1","EWWS780VZXSA1","EWWS890VZXSA1","EWWSC10VZXSA1","EWWSC12VZXSA2","EWWSC13VZXSA2","EWWSC14VZXSA2","EWWSC16VZXSA2","EWWSC17VZXSA2","EWWSC19VZXSA2","EWWSC20VZXSA2"]
["Wydajność chłodnicza","Nom.","","kW","441","493","605","705","783","889","1,039","1,179","1,287","1,390","1,570","1,725","1,876","2,046"]
["Regulator wydajności","Metoda","","","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna","Zmienna"]
["","Minimalna wydajność","","%","20","20","20","20","20","20","20","10","10","10","10","10","10","10"]
["Power input","Chłodzenie","Nom.","kW","87.8","96.8","116.8","138.6","157.7","171.3","207.8","239.2","263.6","282.6","319.6","354.3","396.6","425.5"]
["EER","","","","5.02","5.1","5.18","5.09","4.97","5.19","5","4.93","4.88","4.92","4.91","4.87","4.73","4.81"]
["ESEER","","","","0","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["Wymiary","Jednostka","Głębokość","mm","3,722","3,722","3,750","3,690","3,690","3,822","3,822","4,792","4,792","4,508","4,508","4,750","4,874","4,874"]
["","","Wysokość","mm","2,135","2,135","2,123","2,235","2,235","2,487","2,487","2,296","2,296","2,301","2,350","2,500","2,469","2,493"]
["","","Szerokość","mm","1,178","1,178","1,179","1,189","1,189","1,303","1,303","1,484","1,639","1,579","1,580","1,610","1,704","1,769"]
["Ciężar","Jednostka","","kg","2,968","2,911","3,102","3,470","3,451","4,257","4,552","5,860","6,240","6,520","6,920","7,530","7,790","8,670"]
["","Ciężar operacyjny","","kg","3,098","3,006","3,274","3,648","3,611","4,518","4,860","6,370","6,760","7,130","7,530","8,300","8,560","9,630"]
["Wodny wymiennik ciepła - parownik","Typ","","","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura"]
["","Objętość wody","","l","70","88","136","134","134","168","199","270","270","320","320","380","480","480"]
["Wodny wymiennik ciepła - skraplacz","Typ","","","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura","Zalana obudowa i rura"]
["Sprężarka","Typ","","","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem","Sprężarka jednośrubowa z inwerterem"]
["","Ilość_","","","1","1","1","1","1","1","1","2","2","2","2","2","2","2"]
["Poziom mocy akustycznej","Chłodzenie","Nom.","dBA","97","99","101","105","105","105","107","106","106","107","107","108","109","110"]
["Poziom ciśnienia akustycznego","Chłodzenie","Nom.","dBA","78","80","82","86","86","86","88","87","87","88","88","89","89","90"]
["Czynnik chłodniczy","Typ","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","Charge","","kg","95","95","130","110","170","210","185","250","260","290","290","320","320","350"]
["","Obwody","Ilość","","1","1","1","1","1","1","1","2","2","2","2","2","2","2"]
["","GWP","","","631","631","631","631","631","631","631","631","631","631","631","631","631","631"]