{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":60,"n_cols":9,"rows_kept":60,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYA-DW1P"]
[]
[]
[]
[]
["","","","","","EWYA009DAW1P","EWYA011DAW1P","EWYA014DAW1P","EWYA016DAW1P"]
["Poziom ciśnienia akustycznego","Chłodzenie","","Nom.","dBA","44.0","47.7","50.8","51.0"]
["Elementy hydrauliczne","Przeponowe naczynie wzbiorcze","","Objętość","l","8","8","8","8"]
["Zakres pracy","Strona powietrzna","Chłodzenie","Min.","°CDB","10","10","10","10"]
["","","","Maks.","°CDB","43","43","43","43"]
["","","Grzanie","Maks.","°CDB","25","25","25","25"]
["","","","Min.","°CDB","-25","-25","-25","-25"]
["","Strona wody","Grzanie","Min.","°CDB","9 (7)","9 (7)","9 (7)","9 (7)"]
["","","","Maks.","°CDB","60 (7)","60 (7)","60 (7)","60 (7)"]
["","","Chłodzenie","Maks.","°CDB","22","22","22","22"]
["","","","Min.","°CDB","5","5","5","5"]
["Ładunek czynnika chłodniczego","Na obwód","","","kg","3.80","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6","2.6"]
["Sprężarka","Typ","","","","Sprężarka typu \"swing\" uszczelniona hermetycznie, ze sterowaniem inwerterowym","Sprężarka typu \"swing\" uszczelniona hermetycznie, ze sterowaniem inwerterowym","Sprężarka typu \"swing\" uszczelniona hermetycznie, ze sterowaniem inwerterowym","Sprężarka typu \"swing\" uszczelniona hermetycznie, ze sterowaniem inwerterowym"]
["","Metoda uruchomienia_","","","","Napęd inwerterowy","Napęd inwerterowy","Napęd inwerterowy","Napęd inwerterowy"]
["","Ilość_","","","","1","1","1","1"]
["Powietrzny wymiennik ciepła","Typ","","","","Wysokowydajny żeberkowy i rurowy z wbudowanym dochładzaczem","Wysokowydajny żeberkowy i rurowy z wbudowanym dochładzaczem","Wysokowydajny żeberkowy i rurowy z wbudowanym dochładzaczem","Wysokowydajny żeberkowy i rurowy z wbudowanym dochładzaczem"]
["Ciężar","Jednostka","","","kg","147","147","147","147"]
["EER","","","","","3.35 (1), 5.34 (2)","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Czynnik chłodniczy","GWP","","","","675.0","675.0","675.0","675.0"]
["","Typ","","","","R-32","R-32","R-32","R-32"]
["","Obwody","","Ilość","","1","1","1","1"]
["","Sterowanie","","","","Elektroniczny zawór wzbiorczy","Elektroniczny zawór wzbiorczy","Elektroniczny zawór wzbiorczy","Elektroniczny zawór wzbiorczy"]
["Fan motor","Prędkość","Chłodzenie","Nom.","obr/min_","500","550","650","650"]
["","","Grzanie","Nom.","obr/min_","400","450","550","650"]
["Wydajność chłodnicza","Nom.","","","kW","9.35 (1), 9.10 (2)","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Wodny wym. ciepła","Objętość wody","","","l","2","2","2","2"]
["","Minimalna pojemność wody w systemie","","","l","50 (6)","50 (6)","50 (6)","50 (6)"]
["","Typ","","","","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła","Płytowy wymiennik ciepła"]
["Power input","Chłodzenie","","Nom.","kW","2.79 (1), 1.71 (2)","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["","Grzanie","","Nom.","kW","1.91 (3), 2.43 (4)","2.18 (3), 2.68 (4)","2.46 (3), 3.42 (4)","3.53 (3), 4.56 (4)"]
["Sound power level","Chłodzenie","","Nom.","dBA","65.5","67.0","69.0","69.0"]
["COP","","","","","4.91 (3), 3.71 (4)","4.83 (3), 3.66 (4)","4.87 (3), 3.64 (4)","4.53 (3), 3.51 (4)"]
["Wymiary","Jednostka","","Szerokość","mm","1,380","1,380","1,380","1,380"]
["","","","Głębokość","mm","460","460","460","460"]
["","","","Wysokość","mm","870","870","870","870"]
["Regulator wydajności","Metoda","","","","Zmienna (inwerter)","Zmienna (inwerter)","Zmienna (inwerter)","Zmienna (inwerter)"]
["Ogrz. pom.","Temp. wy. wody dla przec. war. klim. 55°C","Informacje ogólne","Seasonal space heating eff. class","","A++","A++","A++","A++"]
["","","","ηs (sprawność sezonowa ogrzewania pomieszczeń)","%","135","132","134","132"]
["","","","SCOP","","3.44","3.37","3.42","3.37"]
["Wentylator","Przepływ powietrza","Grzanie","Nom.","m³/min","48.0","55.8","70.4","85.0"]
["","","Chłodzenie","Nom.","m³/min","63","70","85","85"]
["Wydajność grzewcza","Nom.","","","kW","9.37 (3), 9.00 (4)","10.6 (3), 9.82 (4)","12.0 (3), 12.5 (4)","16.0 (3), 16.0 (4)"]
["Sprężarka","Metoda uruchomienia_","","","","Inwerter","Inwerter","Inwerter","Inwerter"]
["Power supply","liczba faz","","","","3~","3~","3~","3~"]
["","Częstotliwość","","","Hz","50","50","50","50"]
["","Nazwa","","","","W1","W1","W1","W1"]
["","Napięcie","","","V","400","400","400","400"]
["Uwagi","","","","","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB","(1) - Chłodzenie: EW 12℃; LW 7℃; warunki otoczenia: 35°CDB"]
["","","","","","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB","(2) - Chłodzenie: EW 23℃; LW 18℃; warunki otoczenia: 35°CDB"]
["","","","","","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Warunek: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Warunek: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825","(5) - Według  EN14825"]
["","","","","","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji.","(6) - Zależy od trybu pracy, patrz podręcznik instalacji."]
["","","","","","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy","(7) - Więcej szczegółów widać na rysunku zakresu pracy"]