{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":6,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DF"]
[]
[]
[]
[]
["","","","","","FWC07DAFN5V3--"]
["Wydajność chłodnicza (standardowe warunki)","Użyteczna wydajność, inst. 4-przewod.","","Niska","kW","3.26"]
["","","","Wysoka","kW","5.58"]
["","Wydajność całkowita, inst. 4-przewod.","","Niska","kW","4.35"]
["","","","Wysoka","kW","7.15"]
["Wydajność grzewcza (standardowe warunki)","Wydajność, inst. 4-przewod.","","Niska","kW","5.34"]
["","","","Wysoka","kW","8.82"]
["Pobór mocy","Niska","","","kW","0.02"]
["","Wysoka","","","kW","0.069"]
["Wymiary","Jednostka","","Wysokość","mm","287"]
["","","","Szerokość","mm","837"]
["","","","Głębokość","mm","921"]
["Ciężar","Jednostka","","","kg","27"]
["Wentylator","Przepływ powietrza","","Niski","m³/h","686"]
["","","","Wysoki","m³/h","1,296"]
["Całkowity poziom ciśnienia akustycznego","Niski","","","dBA","36"]
["","Wysoki","","","dBA","52"]
["Poziom ciśnienia akustycznego","Niski","","","dBA","23"]
["","Wysoki","","","dBA","39"]
["Przepływ wody","Chłodzenie","","Niska","l/h","776"]
["","","","Wysoka","l/h","1,295"]
["","Ogrzewanie","","Niska","l/h","459"]
["","","","Wysoka","l/h","759"]
["","Spadek ciśnienia wody","Chłodzenie","Niski","kPa","13"]
["","","","Wysoki","kPa","25"]
["","","Ogrzewanie","Niski","kPa","13"]
["","","","Wysoki","kPa","24"]
["Połączenia instalacji","Woda","","Wlot","","3/4\" BSP (gwint żeński)"]
["","","","Wylot","","3/4\" BSP (gwint żeński)"]
["","Spust","","Śr. zew.","mm","VP25 (Średnica zewnętrzna 32; średnica wewnętrzna 25)"]
["Zasilanie","Typ","","","","230 / 1 / 50"]
["Zasilanie energią elektryczną","liczba faz","","","","1~"]
["Zasilanie","Częstotliwość","","","Hz","50"]
["","Napięcie","","","V","230"]
["Uwagi","","","","","(1) - Chłodzenie: powietrze 27°CDB, 19°CWB; temperatura wody na wlocie 7°C; temperatura wody na wylocie 12°C"]
["","","","","","(2) - Ogrzewanie: 2-rurowe: powietrze 20°CDB, 15°CWB; woda na wlocie 45°C; woda na wylocie 40°C"]
["","","","","","(3) - Ogrzewanie: 4-rurowe: powietrze 20°CDB, 15°CWB; woda na wlocie 65°C; woda na wylocie 55°C"]
["","","","","","(4) - Nie wprowadzać do jednostki wody o temperaturze poniżej 5°C albo powyżej 90°C, gdyż może to spowodować uszkodzenie jednostki"]
["","","","","","(5) - Przepływ powietrza: 20°C DB, 15°C WB; 230V 50Hz 0Pa"]