{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":8,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXM-ATV3"]
[]
[]
[]
[]
["","","","","","FWXM10AATV3","FWXM15AATV3","FWXM20AATV3"]
["Wydajność chłodnicza","7/12°C","","Min.","kW","0.75","1.15","1.32"]
["","","","Śred.","kW","1.36","2.08","2.39"]
["","","","Maks.","kW","2.12","2.81","3.30"]
["Jawna wydajność chłodnicza","7/12°C","","Min.","kW","0.59","0.83","1.02"]
["","","","Śred.","kW","1.04","1.51","1.84"]
["","","","Maks.","kW","1.54","2.11","2.65"]
["Wydajność grzewcza","45/40°C","","Min.","kW","0.82","1.20","1.47"]
["","","","Śred.","kW","1.53","2.16","2.59"]
["","","","Maks.","kW","2.21","3.02","3.81"]
["Pobór mocy","Min.","","","kW","0","0.01","0.01"]
["","Śred.","","","kW","0.01","0.01","0.01"]
["","Maks.","","","kW","0.02","0.02","0.03"]
["Prędkość wentylatora","Min.","","","obr/min_","680.00","680.00","680.00"]
["","Śred.","","","obr/min_","1100.00","1100.00","1100.00"]
["","Maks.","","","obr/min_","1500.00","1500.00","1500.00"]
["Obudowa","Kolor","","","","wbudowany","wbudowany","wbudowany"]
["","Materiał","","","","Bez obudowy","Bez obudowy","Bez obudowy"]
["Wymiary","Jednostka","","Wysokość","mm","576","576","576"]
["","","","Szerokość","mm","725","925","1125"]
["","","","Głębokość","mm","126","126","126"]
["","Jednostka zapakowana","","Wysokość","mm","690","690","690"]
["","","","Szerokość","mm","830","1030","1230"]
["","","","Głębokość","mm","210","210","210"]
["Ciężar","Jednostka","","","kg","12","15","18"]
["","Jednostka zapakowana","","","kg","13","16","19"]
["Opakowanie","Materiał","","","","Karton","Karton","Karton"]
["","Ciężar","","","kg","1","1","1"]
["Wymiennik ciepła","Ilość","","","","1","1","1"]
["","Objętość wew. wężownicy","","","l","0.8","1.13","1.46"]
["","Ładowanie","","Ciśnienie operacyjne","bar","10","10","10"]
["Obwód wody","Średnica połączeń instalacji rurowej","","","in","3/4","3/4","3/4"]
["Obieg wody","Materiał rur","","","","MIEDŹ","MIEDŹ","MIEDŹ"]
["","Ciśnienie","Grzanie","Maks.","bar","10","10","10"]
["Obieg wody - spadek ciśnienia wody","Ogrzewanie","45/40°C","Min.","kPa","1.50","2.70","3.00"]
["","","","Śred.","kPa","4.30","9.30","8.90"]
["","","","Maks.","kPa","9.20","19.10","21.20"]
["","Chłodzenie","7/12°C","Min.","kPa","1.90","2.70","2.50"]
["","","","Śred.","kPa","4.30","9.90","8.80"]
["","","","Maks.","kPa","8.20","17.10","18.00"]
["Obieg wody - natężenie przepływu wody","Ogrzewanie","45/40°C","Min.","kg/h","140.00","210.00","260.00"]
["","","","Śred.","kg/h","270.00","380.00","450.00"]
["","","","Maks.","kg/h","390.00","530.00","660.00"]
["","Chłodzenie","7/12°C","Min.","kg/h","130.00","200.00","230.00"]
["","","","Śred.","kg/h","230.00","360.00","410.00"]
["","","","Maks.","kg/h","360.00","480.00","570.00"]
["Poziom mocy akustycznej","Min.","","","dBA","35","36","36"]
["","Śred.","","","dBA","45","46","47"]
["","Maks.","","","dBA","53.0","54.0","55.0"]
["Zakres pracy","Grzanie","Strona wodna","Min.","°C","30","30","30"]
["","","","Maks.","°C","85","85","85"]
["","Chłodzenie","Strona wodna","Min.","°C","5","5","5"]
["","","","Maks.","°C","18","18","18"]
["","Montaż w pomieszczeniu","Temp. otoczenia","Min.","°CDB","0","0","0"]
["","","","Maks.","°CDB","45","45","45"]
["Syst. kontroli","Pilot na podczerwień","","","","Nie","Nie","Nie"]
["","Wbudowany w jednostkę wewnętrzną","","","","Tak","Tak","Tak"]
["Zasilanie energią elektryczną","liczba faz","","","","1~","1~","1~"]
["Zasilanie","Częstotliwość","","","Hz","50","50","50"]
["","Napięcie","","","V","230","230","230"]
["Pobór mocy elektrycznej","Maks.","","","W","19","20","29"]
["","Tryb gotowości","","","W","3","4","5"]
["Prąd","Maksymalny prąd roboczy","","Grzanie","A","0.16","0.18","0.26"]
["","Maks. prąd roboczy","","Chłodzenie","A","0.16","0.18","0.26"]