{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXMQ-A"]
[]
[]
[]
[]
["","","","","","FXMQ200AXVMB","FXMQ250AXVMB"]
["Wydajność chłodnicza","Wydajność całkowita","","Wysoka prędkość wentylatora","kW","22.4","28.0"]
["Wydajność grzewcza","Wydajność całkowita","","Wysoka prędkość wentylatora","kW","25.0","31.5"]
["Pobór mocy — 50 Hz","Chłodzenie","","Wysoka prędkość wentylatora","kW","0.54","0.65"]
["","Ogrzewanie","","Wysoka prędkość wentylatora","kW","0.54","0.65"]
["Wymiary","Jednostka","","Wysokość","mm","470","470"]
["","","","Szerokość","mm","1490","1490"]
["","","","Głębokość","mm","1100","1100"]
["Ciężar","Jednostka","","","kg","105","115"]
["Obudowa","Kolor","","","","Nie powlekana","Nie powlekana"]
["","Materiał","","","","Galwanizowana blacha stalowa","Galwanizowana blacha stalowa"]
["Wentylator","Natężenie przepływu powietrza - 50Hz","Chłodzenie","Wysoka prędkość wentylatora","m³/min","62","74"]
["","","","Niska prędkość wentylatora","m³/min","41","52"]
["","Spręż dyspozycyjny - 50Hz","","Wysoka","Pa","250","250"]
["","","","Niska","Pa","50","50"]
["","Spręż dyspozycyjny - 60Hz","","Wysoka","Pa","250","250"]
["","","","Niska","Pa","50","50"]
["Czynnik chłodniczy","Typ","","","","R-410A","R-410A"]
["","GWP","","","","2087.5","2087.5"]
["Poziom mocy akustycznej","Chłodzenie","","Poziom mocy akustycznej-=-Chłodzenie-=-Wysoka prędkość wentylatora-=-dBA","dBA","75.0","76.0"]
["Poziom ciśnienia akustycznego","Chłodzenie","","Wysoka prędkość wentylatora","dBA","48.0","48.0"]
["","","","Średnia szybkość wentylatora","dBA","46.5","46.5"]
["","","","Niska prędkość wentylatora","dBA","45.0","45.0"]
["","Ogrzewanie","","Wysoka prędkość wentylatora","dBA","48.0","48.0"]
["","","","Średnia szybkość wentylatora","dBA","46.5","46.5"]
["","","","Niska prędkość wentylatora","dBA","45.0","45.0"]
["Połączenia instalacji rurowej","Ciecz","","Typ","","Połączenie rozszerzające","Połączenie rozszerzające"]
["","","","Śr. zewn.","mm","9.5","9.5"]
["","Gaz","","Typ","","Kołnierz","Kołnierz"]
["","","","Śr. zewn.","mm","19.1","22.2"]
["","Spust","","","","BSP1","BSP1"]
["Standardowe akcesoria","General safety precautions","","","","1","1"]
["","Wire clamp material","","","","1","1"]
["","Spring washer","","","","2","2"]
["","Hexagon head screw","","","","2","2"]
["","Plain washer","","","","8","8"]
["","Hexagon head screw with washer","","","","49","49"]
["","Gas connection pipe","","","","1","1"]
["","Installation and operation manual","","","","1","1"]
["Zasilanie energią elektryczną","Nazwa","","","","VM","VM"]
["","liczba faz","","","","1~","1~"]
["Zasilanie","Częstotliwość","","","Hz","50/60","50/60"]
["","Napięcie","","","V","220-240/220-230","220-240/220-230"]
["Prąd - 50 Hz","Maksymalne amperaże bezpiecznika (MFA)","","","A","6","6"]